## Slide 1: Advances in In-Plant Treatment of Taste-and-Odor Compounds
Djanette Khiari, PhD
Water Research Foundation, USA
Chao Chen, PhD
Tsinghua University, China
10th IWA Symposium on Off-Flavours in the Aquatic Environment, Oct.27 – Nov 1, 2013
NCKU – Tainan, Taiwan

## Slide 2: Important References
Identification and Treatment of Tastes and Odors in Drinking Water (AwwaRF, 1987)
Advances in Taste-and-Odor Treatment and Control (AwwaRF, 1995)

## Slide 3: Treatment Options
Oxidation
  Conventional Cl2, ClO2, KMnO4
  Advanced – O3, O3/H2O2, UV/H2O2
Adsorption
  Powdered Activated Carbon (PAC)
  Granular Activated Carbon (GAC)
Biological Treatment
  Conventional Filter Media
  Biological Activated Carbon (BAC)
Others
  Membranes
  Mixed

## Slide 4: What, Why, When?
Regulations
Consumer perception
Severity, duration, and frequency of the problem
Risk/risk trade-offs
Site and treatment specificity
Performance
Cost (capital and operations)

## Slide 5
Overview of Treatment Technologies
Treatment | Approx. Max Conc. (ng/L) | Episode Duration | Capital Cost | O&M Cost | Usage for T&O (%)
Cl2/ClO2/KMnO4 | < 20 | Short/Long | $ | $ | 18
PAC | < 50 | Short | $ | $$ | 69
Biotreatment | < 50 | Long | $-$$ | $ | 
Ozone/H2O2 | 25 - 75 | Short/Long | $$-$$$ | $-$$$ | 
UV/H2O2 | 25 - 75 | Short | $$-$$$ | $$-$$$ | 
GAC | 25 - 100 | Long | $$-$$$ | $-$$$ | 5
GAC / Multiple Barrier | > 100 | Short | $$$ | $-$$ | 
Multiple Barrier | > 100 | Long | $$$ | $$$ | 
Geosmin and MIB
Corwin & Summers, 2011

## Slide 6: Adsorption
Impacts
Good removal of TCA, geosmin, MIB, IPMP
Competition (TOC, DOC, NOM, BOM, organics)
Other treatment chem (oxidants, coagulants, pH)
Dose
Contact time
PAC
Low
Flexible (when, where, type, how much)
Messy
$/unit removal - jar test
GAC
Moderate
Fixed barrier (can support biological activity)
Easier
$/unit removal - RSSCT
Form
Capital
Application
Handling
Selection
Source
Flash Mix
Clarifiers
Filters
Storage
Notes: But adsorption capacity is affected by:
  Presence of other chemicals that compete for adsorption sites
  Presence of chemicals that coat carbon
  Water quality changes that alter the carbon’s surface characteristics
No DBPs are formed
Water quality changes that alter the odorant’s characteristics
Concentration and characteristics of NOM (Natural Organic Matter)
Presence of CL2, ozone, KMnO4, and chloramines (chlorine and ozone produce surface oxides on carbon)
    More evident at lower odorant levels
    More evident at lower carbon dosages

## Slide 7
Powdered Activated Carbon (PAC)
Performance Drivers for PAC
  Influent TOC concentration
  Influent concentration and treatment objective
  PAC dose
  PAC type (base material)
  Contact time and mixing
 | Dose (mg/L) | Contact Time (min) | Removal (%) | Limitations
PAC | 5 - 30 | 15 - 90 | 40 - > 95 | Feed Rate Oxidant compatibility

## Slide 8
Powdered Activated Carbon (PAC)
Influent TOC Concentration and Contact Time
Cho and Summers, 2007

## Slide 9
Powdered Activated Carbon (PAC)
PAC Dose and Type

## Slide 10
Powdered Activated Carbon (PAC)
Influent Concentration and Treatment Objective

## Slide 11: Superfine Powdered Activated Carbon (SPAC)
Submicron-sized activated carbon: obtained by wet-milling commercially available activated carbon

## Slide 12: MIB Removal
(S-)PAC Dose = 15 mg/L Initial MIB Conc. = 100 ng/L
Overall, smaller as-received PACs did not perform better than traditional PACs
Superfine forms of PAC A and C achieved >89% MIB removal
Dunn et al, 2010

## Slide 13: MIB Removal – equilibrium conditions
(S-)PAC Dose = 15 mg/L Initial MIB Conc. = 100 ng/L
  Grinding as-received PAC to a finer particle size
    enhanced adsorption kinetics
    did not increase equilibrium uptake capacity for MIB
  S-PACs would be beneficial for MIB removal at short contact times
Dunn et al, 2010

## Slide 14: MIB Removal
Similar MIB removal trends in CCR and LM waters with S-PAC achieving higher MIB removal than PACs
Decreased MIB removal in LM water possibly due to higher adsorption competition between NOM and MIB (higher NOM concentration in LM water)
CCR
LM
(S-)PAC Dose = 15 mg/L Initial MIB Conc. = 100 ng/L
Dunn et al, 2010

## Slide 15
Granular Activated Carbon (GAC)
Application | EBCT (min) | Removal (%) | Use Rate (lb/1,000 gal) | Media size | Limitations
Filter Adsorber | 2 - 10 | > 95 | 0.4 – 1.1 | 8x30 ES= 0.90 mm | Oxidant compatibility Media replacements are more difficult May need sand layer Backwashed
Post-Filter Adsorber | 5 - 30 | > 95 | 0.25 – 1.0 | 12x40 ES= 0.65 mm | Cost/space/hydraulic head Oxidant compatibility

## Slide 16
Granular Activated Carbon (GAC)
Performance Drivers
  Influent TOC concentration
  Influent concentration & treatment objective
  Design and operation strategy
  GAC type

## Slide 17
Granular Activated Carbon (GAC)
Operation Strategy
Operation | Advantages | Disadvantages
Continuous | DBP formation control Lower Cl2 demand 0.5 log Crypto credit (PFA only) | Reduced TO adsorption capacity* * can be offset by GAC change-out prior to episode
Intermittent | Maximum TO adsorption capacity | Large capital investment for intermittent use
Biological | Possible removal by both adsorption and biodegradation? Possible bio-regeneration of adsorption capacity?? | More frequent backwashes Underdrain clogging? Possibility of higher HPC counts in finished water?
Corwin and Summers, 2011

## Slide 18: Oxidation
Source
Flash Mix
Clarifiers
Filters
Storage
Distribution
Permanganate
Chlorine
Chloramines
Chlorine dioxide
Ozone
UV
Advanced oxidation (O3/H2O2, UV/H2O2)

## Slide 19: Permanganate (MnO4-)
Source
Flash Mix
Clarifiers
Filters
Storage
Distribution
Fishy, grassy, cucumber
Reduces Chlorine demand
Reduces AC demand
THMs
Colored water
Adsorption (???)_

## Slide 20
Chlorine
Source
Flash Mix
Clarifiers
Filters
Storage
Distribution
Marshy/Swampy/Septic/Sulfurous/Fishy
Disinfection
Algae control
Chlorinous
Medicinal
Biofilm control
DBP formation

## Slide 21: Chlorine Dioxide (ClO2)
Source
Flash Mix
Clarifiers
Filters
Storage
Distribution
Marshy/Swampy/Septic/Sulfurous/Medicinal
Disinfection and algae control
Fe and Mn control
Kerosene
Cat urine
ClO2-/ClO3- formation

## Slide 22: Advanced Oxidation Processes (AOPs)
An effective process for disinfection and chemical oxidation
AOPs work by creating hydroxyl radicals (•OH)
Complex chemistry
Several Technologies
  UV/H2O2, UV/O3, UV/HOCl, etc.
  Ozone/H2O2, Ozone/NOM, Ozone/pH

## Slide 23: Ozone/AOPs
Pre-Ozone
Basin
Flash
Mix
Clarifiers
Inter-Ozone
Basin
Filters
Post-Ozone
Basin
Storage
Higher Dose
Unstable Residual
Easier Hydraulics
Lower Dose
Stable Residual
Difficult Hydraulics
Lowest Dose
Stable Residual
Fragrant/Sweet
Medicinal
AOC
BrO3- formation

## Slide 24: Ozone Oxidation of MIB and Geosmin
Ozone is effective for MIB and geosmin Direct ozonation is very slow for oxidizing MIB and geosmin
But OH radical is quite effective
Direct ozonation better for toxins
Observed MIB and Geosmin ozone oxidation a result of Advanced Oxidation (AOP)
Compound | kO3 (M-1s-1) | kOH (M-1s-1)
MIB | N/A | 8.2x109
Geosmin | N/A | 1.4x1010

## Slide 25: Ultraviolet (UV)
1
10
100
1,000
10,000
Applied UV Dose (mJ/cm2)
Crypto. (>2-log)
Virus (2-log)
NDMA (90%)
Geosmin/MIB (90%)
MTBE (90%)
Source
Flash
Mix
Clarifiers
Filters
Storage
Distribution

## Slide 26: UV AOP for Taste and Odor
UV Photolysis
UV Advanced Oxidation
Rosenfeldt and Linden, 2005

## Slide 27: AOP performance
Ozone + Peroxide AOP
Extra 30% oxidation
UV + Peroxide AOP
AWWARF, 2005
Rosenfeldt and Linden, 2004

## Slide 28: Biological Filtration
Principle: Odorants at low concentrations are utilized by microorganisms as secondary substrates when the biodegradable organic matter is sufficient to serve as the primary substrate.
Biotreatment | Contact Time (min) | Acclimation Period | Removal (%) | Limitations
Conventional Media | 5 – 10 | > 4 months | 30 - > 95 | Temperature Substrate availability Influent concentration fluctuations
Biological Activated Carbon (BAC) in FA | 5 – 10 | > 4 months | 60 - > 95 | Temperature Substrate availability
Corwin and Summers, 2011

## Slide 29: Pilot Testing
(AWWARF, 2005 –Westerhoff)

## Slide 30: Pilot Testing
Biofilters receiving 4 different feed waters, biologically active carbon (GAC) removed more MIB and geosmin) than GAC/sand or anthracite/sand biofilter
The control anthracite/sand (A/S) biofilter received chlorinated water and achieved minimal MIB degradation.
Longer EBCCT improved removal
Finding #2: Pilot tests required at least 2 months of constant MIB exposure to become acclimated and biologically stable. Longer EBCTs and higher temperatures improved MIB degradation. MIB & geosmin biodegradation was modeled as
secondary substrates.
Finding #3: Filter biomass density was a good
indicator for MIB removal in some pilot tests.
More biomass equated to improved removal.
Backwashing practices affected biomass density, with more benefit of using non-chlorinated water

## Slide 31: Pilot Testing
Pilot tests required at least 2 months of constant MIB exposure to become acclimated and biologically stable.
Longer EBCTs and higher temperatures improved MIB degradation
Filter biomass density was a good indicator for MIB removal in some pilot tests. More biomass equated to improved removal.
Backwashing practices affected biomass density, with more benefit of using non-chlorinated water

## Slide 32: Membrane Treatment
Removal by Size and Charge
    Membrane effective pore size
    Membrane surface charge (Zeta potential)
    Compound charge (pKa)
    Charges depend on water pH
Microfiltration and Ultrafiltration
  Particle removal membranes
  Limited removal by charge repulsion
Reverse osmosis may remove minerals and organics producing unpalatable water
Highly corrosive to metal plumbing

## Slide 33
Courtesy of Gayle Newcombe

## Slide 34: Caution!!!
Algal metabolites can be:
  Intracellular: Contained within the cell
  Extracellular : Dissolved (extracellular)
Cells can be removed by physical processes (relatively easy)
Extracellular, dissolved metabolites can be removed by physical, chemical or biological processes (not so easy)
Algae vs. Algal Metabolites

## Slide 35: Zeolites
Primary building blocks are TO4 tetrahedra (T is Si4+ or Al3+) linked via their oxygen atoms to other tetrahedra
↓
↓
Structural subunits form crystalline framework
Pore dimensions defined by the ring size of the aperture
“10 ring" is a closed loop built from 10 tetrahedrally coordinated Si4+(or Al3+) atoms and 10 oxygen atoms
: Si4+ or Al3+
:Oxygen

## Slide 36: Zeolite framework types
Silicalite framework type:
Pore dimensions:
0.53 x 0.56 nm and 0.51 x 0.55 nm
Mordenite framework type:
0.65 x 0.70 nm
Beta framework type:
0.76 x 0.64 nm
Y framework type:
0.74 nm diameter windows
1.3 nm supercages
Source: http://topaz.ethz.ch/IZA-SC/StdAtlas.htm

## Slide 37: Zeolites
SiO2/Al2O3 ratio the determines hydrophobicity and acidity
of the zeolite
low SiO2/Al2O3 → negative framework charge
  hydrophilic character → not effective for the adsorption of organic contaminants but suitable for cation exchange
  more acidity → suitable for surface reactions
high SiO2/Al2O3 → low negative or neutral framework charge
  hydrophobic character → suitable for the adsorption of organic contaminants
  less acidity → not very reactive

## Slide 38
Experiments with 14C-MIB assess overall removal of 14C from solution but do not provide information about the reactive removal of MIB
Experiments with 12C-MIB were conducted to specifically track MIB removal

## Slide 39: Clearly, 12C data differed from the 14C data when testing mordenite zeolites!!
Yuncu and Knappe, WaterRF 2005

## Slide 40
Discrepancies between 14C-MIB and 12C-MIB data may suggest that a reaction removal mechanism other than adsorption contributes to MIB removal
H+
H+
H+
H+
MIB
1-methylcamphene (1MC)
2-methylenebornane (2MB)
2-methyl-2-bornene (2M2B)
Non-odorous products
Acidic zeolite surface
Yuncu and Knappe, WaterRF 2005

## Slide 41: www.WaterRF.org
dkhiari@WaterRF.org